## DropDownList (hidden)
[9 empty] | MIP Check Boc | Disposal | Lift | Effluent filter
[9 empty] | 2 | FALSE | FALSE | FALSE
0 | 1 | 0 | Coarse Sand |  | 0
1 | 2 | 1 | Loamy Sand |  | 1 | 0 | 1.5 | [7 empty] | 1000 |  | 0.5
2 | 3 | 2 | Med Sand | AM | 2 | 5 | 2 |  |  | 1 |  | 1.2 | 2.5 | 0.1875 | 1500 | 0.42 | 1 | 0.045 | 1 | 0.83
3 | 4 | 3 | Fine Sand | PM | 3 |  | 3 |  |  | 1.5 |  | 0.79 | 3 | 0.21875 | 1600 | 0.56 | 1.5 | 0.078 | 1.25 | 1.67
4 | 5 | 4 | Sandy Loam |  | 4 |  |  |  |  | 2 |  | 0.6 | 3.3 | 0.25 | 2000 | 0.59 | 2 | 0.11 | 1.5 | 1.27
5 | 6 | 5 | Loam |  | 5 |  |  |  |  | 2.4 |  | 0.5 | 4 |  | 2250 | 0.74 |  | 0.17 | 2 | 2
6 | 7 | 6 | Silt Loam |  | 6 |  |  |  |  | 2.67 |  | 0.45 | 5 |  | 3000 | 0.8 |  | 0.25 |  | 2.2
7 | 8 | 7 | Silt |  | 7 |  |  |  |  | 5 |  | 0.24 |  |  | 4000 | 0.94 |  | 0.38 |  | 4.2
8 | 9 | 8 | Clay Loam |  | 8 | [10 empty] | 1.04 |  | 0.66
9 | 10 | 9 | Silty or Sandy Clay Loam |  | 9 | [10 empty] | 1.26
10 |  | 10 | Silty or Sandy |  | 10 | [10 empty] | 1.65
|  |  | Clay |  | 11
[5 empty] | 12 |  |  | E-20 Volume of Liquid in Pipe
[5 empty] | 13 |  |  | Pipe Diameter | Liquid per foot
[5 empty] | 14 |  |  | inches | gallons
[5 empty] | 15 | 2 |  | 1 | 0.045
[5 empty] | 16 |  |  | 1.25 | 0.078 | [7 empty] | 1 |  |  |  | FALSE | FALSE | FALSE
[5 empty] | 17 |  |  | 1.5 | 0.11 |  |  |  | 1.25 | 0.078
[5 empty] | 18 |  |  | 2 | 0.17
[5 empty] | 19 |  |  | 2.5 | 0.25
[5 empty] | 20 |  |  | 3 | 0.38
[5 empty] | 21 |  |  | 4 | 0.66
22
23
24
25
2
3
[7 empty] | 4 |  |  | 4 | 4
[7 empty] | 5 |  |  | 3.85 | 4.17
[7 empty] | 6 |  |  | 3.7 | 4.35
[7 empty] | 7 |  |  | 3.57 | 4.54
[7 empty] | 8 |  |  | 3.45 | 4.76
[10 empty] | 3.33 | 5
[10 empty] | 3.23 | 5.26
[10 empty] | 3.12 | 5.56
[10 empty] | 3.03 | 5.85
[10 empty] | 2.94 | 6.25
[10 empty] | 2.86 | 6.67
[10 empty] | 2.78 | 7.14
[10 empty] | 2.7 | 7.69

## Intro
Instructions for SSTS Basic Design Forms
These Design forms included in this file are intended to meet the Grant Counties SSTS rules. There are 13 worksheets and additional supporting information in the SSTS Basic Design Form Workbook, they are:
2014 version | 1. Site Evaluation |  | 5. Trench or Bed | 9. Pressure Distribution | 13. Summary Sheet
| 2. Soils |  | 6. Mound System <1% | 10. Pump Sheet
| 3. Site Map |  | 7. Mound System >1% | 11. Non-Level
| 4. Percolation Test |  | 8. At Grade System | 12. Dosing Chamber
These worksheets were created in Microsoft Excel. You must have a software program that can open .xls documents to use these forms. If you do not have Microsoft Excel, you can download a similar program named OpenOffice online: http://www.openoffice.org/
There are two ways you can utilize this workbook:
1. You can use the Excel worksheet on a computer and fill in the values on a computer & print out the results or email them. Using this function you must be sure to enable macros if asked this by Excel, or
2. You can print blank copies of the worksheets and fill them out by hand.
SECURITY LEVEL & MACROS
This file contains macros which are imbedded formulas to do some of the calculations. In order for these to work:
1. Your security level must be medium or low (not the default of high). This can be changed under Tools, Macro, Security. In Office 2007, click the Microsoft Office Button, then click the Excel Options. Select the Trust Center, Settings, and then click Macro Settings to enable.
2. If prompted enable the macros.
INPUTS
In each worksheet, you will notice each cell is colored either blue (or grey depending on your system settings) or yellow.
Yellow cells are user input cells, that is, these are the cells where you as the designer must manually enter the value that the worksheet is requesting. If you begin on each sheet on the first yellow cell, you can then Tab through the rest of the form and you will tab only through cells that require you to enter information.
Blue cells are cells that will fill in automatically as you enter values into the yellow cells.
CHECK BOXES
Many of the worksheets have check boxes that one may check on the computer. If these are not working, you are most likely is in "design mode" in excel. To fix this, from the menu, select View, Toolbars, and then select "Control Toolbox". Now a new toolbar will appear in your menu bar. There is a button that looks like a ruler and a speed square. Click it to get out of design mode. Now the check boxes should work.
DROP DOWN MENUS
Some of the yellow cells have a drop-down menu function. A small arrow pointing downwards will appear in the lower right corner of the cells with a drop-down menu. You MUST choose one of the values in the drop-down menu. To erase the value, simply highlight the cell and press the Delete key on your keyboard.
NOTE: Most of the cells in this workbook have a great deal of complex formatting and formulas in the background. If you alter the formulas, the workbook will not function properly. It would be a good idea to copy this workbook and always work with the the copy, so the original can be utilized for back-up purposes only.
PRINTING
The worksheets should display and print at 100%. This makes the worksheets readable and able to be filled in by hand. The worksheets can be printed in either color or black and white. You may need to set your computer/printer to grayscale option or you may wish to change the colored portions of the worksheets. Each sheet that is part of your design must be printed separately as there is not a way to print them all at one time.
SAVING
Each time a design is done the file should be saved with a unique file name. Keep an original version of the workbook with no data entered. To have a version which can not be altered you can create at PDF. Creating a PDF requires the full version of Adobe Acrobat which is software you may not have. The other option is to go to "Tools"..."Protection"..."Protect Worksheet" and save the file for that particular job which it what the overall plan for how to do this.
CREDITS
Design based on the University of Minnesotas 2014 SSTS Excel File. Modified by Jared House, Greg Lillemon, and the County for local use.

## Site Evaluation
| Site Evaluation Form | [6 empty] | Tax ID # | 2345
Property Owner(s) | [6 empty] | Phone Number:
911 Address | [6 empty] | Tax ID #: | 2345
Section |  |  | Township |  |  |  | Legal Description
Designer
Installer |  |  |  |  | License # | 45678 |  | Date
Location Information
(check all that apply)
Design Information
System Type
No. of bedrooms (if applicable) |  |  |  | 3 | (includes possible additions)
Estimated flow |  |  |  | 450 | gpd see chart A-1
Well casing depth |  |  |  | 50 | feet
Water using devices
(check all that apply)
Discharge Location (if checked)
Site Evaluation
Soil texture classification: |  | Clay Loam |  |  |  | Unnatural soil (check)
Type of observation (check) | [5 empty] | Vegetation type (check)
Parent material (check)
Slope form (check)
Drainage (check)
Located in floodplain (check)
| Depth to limiting layer |  |  | 48 | inches |  | 4 | feet
| % Slope |  |  | 3 | %
| Maximum depth of system: |  |  | 12 | inches
| Soil sizing factor (SSF): |  |  | 2.2 | gpd/ft2 (See Table D-15)
Was a perc test done ?
| Depth of Test |  |  |  | inches |  |  | MPI
| Estimated Perc |  |  | 45 | MPI |  | Soil loading rate |  | 0.45 | gpd/ft2
(if test not completed) | [8 empty] | (See Figure D-33)
Septic Tank Capacity |  |  |  | 1500 | Gallons |  | Number of Tanks |  | 1
(see figure C-1)
Effluent filter | [6 empty] | Linear loading rate |  | 6 | gpd/ft
(See Figure D-42)
System Type selection is REQUIRED to make spreadsheet work correctly
Yes?
Mound Percent
Mound < 1%
Mound > 1%
Trench or Bed
At Grade
Establishment
Location Information
Shoreland
In Wellhead Protection Area
Dwelling
Replacement System
New Home Construction
Observation Type
Pit
Probe
Boring
Parent Material
Till
Loess
Bedrock
Alluvium
Outwash
Vegetation Type
Wet
Dry
Unknown
Slope Form
Summit
Back
Foot
Toe
Shoulder
Drainage
Good
Poor
Ponding
Flooding
Fair
Unnatural
Yes
No
Perc Test
Yes
No
Floodplain
Yes
No
Laundry / Large Tub on 2nd Floor
Water Using Devices
Garbage Disposal
Dishwasher
Large Bathtub
Water Softener
Sump Pump
High Eff. Furnace
Jucuzzi / Hottub
Lift Station (before tank)

## soils
Soil Data |  |  |  | Tax ID#: | 2345
911 Address:
Soil Survey Data
Map Unit
Boring/Pit 1 |  | Elevation: |  |  | Location:
Soil Depth (Inches) | Boring Elevations | Texture | Color | Mottle Color(s) | Structure | Consistence
Boring/Pit 2 |  | Elevation: |  |  | Location:
Soil Depth (Inches) | Boring Elevations | Texture | Color | Mottle Color(s) | Structure | Consistence
Boring/Pit 3 |  | Elevation: |  |  | Location:
Soil Depth (Inches) | Boring Elevations | Texture | Color | Mottle Color(s) | Structure | Consistence

## Site Map
Site Evaluation Map
Scale:
List any construction issues:
Mapping Checklist |  | 911 Address: | [6 empty] | Tax ID #: |  | 2345
Map scale: |  |  | indicate north |  | show slope |  |  | % direction
|  |  |  | TANK |  |  | DRAINFIELD
| Size |  |  |  |  | Gls |  |  |  | Ft
| Setback to OHWL |  |  |  |  | Ft |  |  |  | Ft
| Setback to Wetland |  |  |  |  | Ft |  |  |  | Ft
| Setback to dwelling |  |  |  |  | Ft |  |  |  | Ft
| Setback to non-dwelling |  |  |  |  | Ft |  |  |  | Ft
| Setback to nearest property line |  |  |  |  | Ft |  |  |  | Ft
| Setback to road right-of-way |  |  |  |  | Ft |  |  |  | Ft
| Setback to nearest well |  |  |  |  | Ft |  |  |  | Ft

## PercTest
Percolation Test |  |  |  |  | Tax ID #: | 2345
911 Address:
Homeowner Name
Address
Percolation Test Performed by
| Company Name |  |  |  |  | License Number | 45678
| Test Hole # |  | Diameter of hole |  | inches
| Location |  |  |  |  | Depth of test | inches
Method of scratching sidewall
| Depth at bottom of hole |  |  | inches | Depth of gravel at bottom |  | inches
| Date presoak started |  |  |  | Starting at
| Depth of initial water filling |  |  | inches (above hole bottom)
Method used to maintain 12" of water depth in hole for 4 hours
| Date presoak ended |  |  |  | Ending at
| Date perc readings conducted |  |  |  | Starting at
| Maximum depth above hole bottom during test |  |  |  | inches
| Surface elevation (in reference to benchmark): |  |  |  | feet
Directions: Enter elapsed time and drop in water level and the rest will be calculated
# | Elapsed Time (min) | Time Interval (min) | Drop in Water Level (inches) | Percolation Rate (mpi) | % Difference | 10% Goal Reached*
1 |  | 0 |  | 0 | NA | NA
2 |  | 0 |  | 0 | 0 | 0
3 |  | 0 |  | 0 | 0 | 0
4 |  | 0 |  | 0 | 0 | 0
5 |  | 0 |  | 0 | 0 | 0
6 |  | 0 |  | 0 | 0 | 0
7 |  | 0 |  | 0 | 0 | 0
8 |  | 0 |  | 0 | 0 | 0
* 3 consecutive percolation rates must be within 10% or less of each other
| Take the highest score that is within 10% |  |  |  |  | MPI

## Trench or Bed
Trench or Bed | [5 empty] | Tax ID #: | 2345
911 Address:
1. | Flow
A. | Estimated Flow | 450 | gpd
2. | Minimum Septic Tank Capacity
B. | Septic tank capacity (Fig C-1) |  | 1500 | gallons |  | # of tanks/compartments |  |  | 1
C. | Effluent filter (yes/no) |  | No
3. | Pump Tank Specifications
D. | Pump tank needed (yes/no) |  | Yes |  |  | Minimum size if needed |  | 38.48 | gallons
4. | SOILS (Site evaluation data)
E. | Depth to restricting layer = |  | 4 | ft
F. | Maximum depth of system Item E - 3 ft = |  |  | 4 | - | 3 | = | 1 | ft
G. | Texture | Clay Loam |  |  |  | Percolation Rate |  | 45 | mpi
if available
H. | SSF | 2.2 | ft2/gpd
I. | % Slope | 3 | %
5. | System Information
| System Type (Check boxes) |  |  | Distribution Media Type |  |  |  | Method of Distribution
Select one type of system
6. | TRENCH OR BED BOTTOM AREA
J. | For trenches with 6 inches of side wall beneath the pipe or chamber system
| A x H = | 450 | gpd x | 2.2 |  | ft/gpd = |  | NA | ft2
K. | For trenches with 12 inches of sidewall:
| A x H x 0.8= | 450 | gpd x | 2.2 |  | ft/gpd x 0.8 = |  | NA | ft2
L. | For trenches with 18 inches of sidewall:
| A x H x 0.66= | 450 | gpd x | 2.2 |  | ft/gpd x 0.66 = |  | NA | ft2
M. | For trenches with 24 inches of sidewall:
| A x H x 0.6= | 450 | gpd x | 2.2 |  | ft/gpd x 0.6 = |  | NA | ft2
N. | For gravity beds with 6 or 12 inches of rock below the pipe;
| 1.5 x A x H = 1.5 x |  | 450 | gpd x |  | 2.2 |  | ft/gpd = | NA | ft2
O. | For pressure beds with 6 or 12 inches of rock below the pipe;
| A x H = | 450 | gpd x | 0 |  | ft/gpd = |  | NA | ft2
7. | Trench and Bed Dimensions
P. | Select required square feet of bottom area required based on depth of rock/gravelless pipe or height of chamber slats
|  |  | 990 | ft2 | Self generate from above selection
(must use 6" of rock square footage for beds)
Q | Select width of trench or bed |  | 15 | ft
(use 3' for gravelless pipe, width of chamber or width of excavation for rock in trenches &
beds can not be wider the 25')
R. | For trenches or pressure beds the lineal feet required = required square footage / width of bottom of trench or bed
|  | 990 | ft2 / | 15 |  | ft = |  | NA | lineal feet
S. | For gravity beds the lineal feet required = required square footage / width of bed
|  | 990 | ft2 / | 15 |  | ft = |  | NA | lineal feet
8. | Rock Sizing and Volume
T. | Depth of media below pipe |  | 1 | ft
Cubic feet of rock needed = Rock depth below distribution pipe plus 0.5 foot times bottom area:
(Rock depth + 0.5 foot) x Area (J, K, L, M)
| ( | 1 | ft + 0.5 ft) x | 990 | ft2 = | 1485 | ft3
Volume in cubic yards = volume in cubic feet divided by 27
|  | 1485 | / 27 = | 55 |  | yd3
Weight of rock in tons = cubic yards times 1.4
|  | 55 | x 1.4 = | 77 |  | tons
| Add in 10% extra for constructability = 1.1 X |  |  | 77 | = | 84.7 | tons
System Type
Pressure Bed (<6% slope)
Gravity Bed (<6% slope)
Trenches
Distribution Media
Rock
Chamber
Other:
Method of Distribution
Pressure
Drop Boxes
Dist. Box (<3% slope)
Other :

## Mound <1%
Mound (Less than or equal to 1%) |  |  |  |  | Tax ID #: | 2345
911 Address:
A. | FLOW
|  | Estimated | 450 | gpd
|  | or measured |  | x 1.5 (safety factor) = |  | gpd
B. | SEPTIC TANK LIQUID VOLUMES
[13 empty] | 1.5" inspection pipe |  | 18 " at peak - top 6" topsoil
Septic tank capacity |  |  | 1500 | gallons
Number of tanks/compartments |  |  | 1
12" cover - top 6" topsoil
C. | SOILS (Site evaluation data) | [11 empty] | 1
Original grade
4
1. | Depth to restricting layer= |  |  | 4 | feet | [6 empty] | Restrictive layer
2. | Depth of percolation tests = |  |  | NA | inches | [5 empty] | berm: | 12 |  | 10 |  | berm: | 12
3. | Texture |  |  | Clay Loam | [9 empty] | absorption width: | 27
4. | Soil loading rate (see Figure D-33) |  |  | 0.45 | gpd/ ft2
5. | Percolation rate |  |  | 45 | MPI
6. | % Land Slope |  |  | 3 | %
D. | ROCK LAYER DIMENSIONS | [12 empty] | Mound Detail: Land slope < or = to 1%
1. | Required area of rock layer:
Multiply average design flow (A) by 0.83
12
|  | 450 | gpd x 0.83 ft2/gpd = |  | 380 | ft2
2. | Rock layer width
| 0.83 ft2/gpd x Linear Loading Rate (LLR) | [11 empty] | Rockbed
[11 empty] | 12 |  | Width: | 10 |  | Total absorption width: |  | 12
|  | 0.83 ft2/gpd x |  | 12 | = | 10 | ft |  |  | Total |  |  | Length: | 38 |  | 27
Width:
3. | Length of rock layer | [8 empty] | 34
| area divided by width | [15 empty] | Rockbed setback
8.5
|  | 380 | ft2 / | 10 | feet = | 38 | ft | [6 empty] | 12 |  |  | (all sides)
E. | ABSORPTION WIDTH
|  | Absorption Ratio (Fig. D-33): |  | 2.67 | [9 empty] | Total length: | 62
1. | Absorption width
absorption ratio (see Figure D-33) times rock layer width
| 2.67 | x | 10 | ft = | 27 | ft |  |  |  | Notes:
F. | MOUND SLOPE WIDTH & LENGTH (Less than or equal to 1%)
1. | Absorption width (F): |  | 27 | feet
2. | Minimum mound size
a. Depth of clean sand at upslope edge of rock layer
3 feet minus distance to restricting layer(C1)
| 3 | ft - | 4 | ft = | 1 | ft
b. Mound height at the upslope edge of rock layer
depth of clean sand for separation (G2a) plus depth of rock layer (1 foot) plus depth of cover (1 foot)
|  | 1 | ft+1ft+1ft = | 3 | ft
c. Berm width
upslope mound height(G2b) times 4 (4 is recommended, but could be 3-12)
|  | 3 | x 4 = | 12 | ft
d. Total landscape width
berm (G2c) width plus rock layer width (D2) plus berm width (G2c)
|  | 12 | feet + | 10 | feet + | 12 | feet = | 34 | ft
e. Additional width necessary for absorption
the absorption width (F) minus the landscape width (G2d)
|  | 27 | feet - | 34 | feet = | -7 | ft
if number is negative (<0) skip to g
f. Final berm width
additional width (G2e) plus the berm width (G2c)
|  | -7 | feet + | 12 | feet = | 5 | ft
g. Total mound width
berm width(G2f or G2c) plus rock layer width (D2) plus berm width (G2f or G2c)
|  | 12 | ft + | 10 | ft + | 12 | ft = | 34 | ft
h. Total mound length
berm (G2f or G2c) plus rock layer length (D3) plus berm (G2f or G2c)
|  | 12 | ft + | 38 | ft + | 12 | ft = | 62 | ft
i. Setbacks from the rockbed
the absorption width (F) minus the rock bed width (D2) divided by 2
|  |  | 27 | feet - | 10 | feet) / 2 = |  | 8.5 | ft
| Final Dimensions (slope < 1%) |  |  | 34 | ft x | 62 | ft
G. | SAND VOLUME
| 1. | Upslope Volume + Volume under rockbed + Downslope Volume
|  | 2 | ft x | 12 | ft x | 62 | ft / 2 = | 744 | ft3
b. Volume under rockbed
(average depth of sand under rock) x (rockbed width) x (mound length) = ft3
|  | 1 | ft x | 10 | ft x | 62 | ft = | 620 | ft3
c. Downslope Volume
(depth of clean sand + 1) x (downslope berm) x (mound length) / 2 = ft3
|  | 2 | ft x | 12 | ft x | 62 | ft / 2 = | 744 | ft3
[6 empty] | Total cubic feet: | = | 2108 | ft3
| 2. | Cubic yards
Divide ft3 by 27 ft3/yd3
|  |  | 2108 | / 27 = | 78.0741 | yds3
| 3. | Weight of sand in tons
Multiply cubic yards by 1.4
|  |  | 78.0741 | yds3 x 1.4 | 109.3037 | tons
| 4 | Add 10% for Constructability
|  |  | 109.3037 | tons x 1.1 = | 120.2341 | tons
H. | ROCK VOLUME
1. | Cubic feet of rock
Multiply rock area by rock depth
|  | 380 | X | 1 | ft = | 380 | ft3
Depth of rock layer
2. | Cubic yards
Divide ft3 by 27 ft3/yd3
|  | 380 | ft3 / 27 = | 14.0741 | yd3
3. | Weight of rock in tons;
Multiply cubic yards by 1.4
|  | 14.0741 | yd3 X 1.4 ton/yd3 = |  | 19.7037 | tons

## Mound>1%
Mound (Greater than 1%) |  |  |  |  | Tax ID #: | 2345
911 Address:
Mound Detail: Land slope > 1%
A. | FLOW
| Estimated |  | 450 | gpd | [9 empty] | Upslope berm: | 8.3
| or measured |  |  | x 1.5 (safety factor) = |  | gpd
Rockbed
B. | SEPTIC TANK LIQUID VOLUMES
[10 empty] | Total |  |  | Width: | 10
[10 empty] | Width: |  | 8.3 | Length: | 38 |  | 8.3
35.3
| Septic tank capacity |  | 1500 | gallons | [9 empty] | Downslope absorption width:
| # of tanks/compartments |  | 1 | [10 empty] | 17
C. | SOILS (Site evaluation data)
[12 empty] | Downslope berm: | 17
[13 empty] | Total length: | 54.6
1. | Depth to restricting layer = |  |  | 4 | feet
2. | Depth of percolation tests = |  |  | NA | inches
3. | Texture |  |  | Clay Loam
4. | Soil loading rate |  |  | 0.45 | gpd/ ft2
5. | Percolation rate |  |  | 45 | MPI
6. | % Land Slope |  |  | 3 | %
D. | ROCK LAYER DIMENSIONS
1.5" inspection pipe
1. | Required area of rock layer:
|  | 450 | gpd x 0.83 ft2/gpd | = | 380 | ft2
1
2. | Rock layer width
| 0.83 ft2/gpd x Linear Loading Rate (LLR) | [10 empty] | 4
|  | 0.83 ft2/gpd x |  | 12 | = | 10 | ft |  |  |  | 8.3 |  | 10 | 17
3. | Length of rock layer | [12 empty] | 27
absorption width
|  | 380 | ft2 / | 10 | feet = | 38 | ft
E. | ABSORPTION WIDTH
Notes:
|  |  | Absorption ratio: | 2.67 | Table D-33
1. | Absorption width ( absorption ratio times rock layer width)
| 2.67 | x | 10 | ft = | 27 | ft
F. | MOUND SLOPE WIDTH & LENGTH (Greater than 1%)
1. | Downslope absorption width (absorption width minus rock layer width)
| 27 | feet - | 10 | feet = | 17 | ft
2. | MOUND SIZE (UPSLOPE)
a. Depth of clean sand at upslope edge of rock layer (3 feet minus distance to restricting layer(C1))
| 3 | ft - | 4 | ft = | 1 | ft
b. Mound height at the upslope edge of rock layer
(depth of clean sand for separation (G2a) at upslope edge plus depth of rock layer (1 foot) to depth of cover (1 foot)
|  | 1 | ft + 1ft + 1 ft = | 3 | ft
c. Upslope berm multiplier based on land slope
|  | Selected berm multiplier: |  | 2.75 | Figure D-34
d. Upslope width
(berm multiplier(G2c) times upslope mound height(G2b):)
|  | 2.75 | x | 3 | ft = | 8.3 | ft
MOUND SIZE (DOWNSLOPE)
e. Drop in elevation
rock layer width (D2) times percent landslope(C5) / 100
|  | 10 | ft x | 3 | % / 100 = | 0.3 | ft
f. Downslope mound height
depth of clean sand for slope difference (G2e) at downslope rock edge
plus the mound height at the upslope edge of rock layer
|  | 0.3 | ft + | 3 | ft = | 3.3 | ft
g. Downslope berm multiplier based on percent land slope
|  | Selected berm multiplier: |  | 2.75 | Figure D-34
h. Downslope width = downslope multiplier(G2g) times downslope mound height(G2f)
|  | 2.75 | x | 3.3 | = | 9.1 | ft
| i. Select greater of G1 and G2h as the downslope width |  |  |  |  | 17 | ft
j. Total mound width
the sum of upslope (G2d) width plus rock layer width (D2) plus downslope width (G2i)
|  | 8.3 | ft + | 10 | ft + | 17 | ft = | 35.3 | ft
k. Total mound length
upslope width (G2d) plus rock layer length (D3) plus upslope width (G2d)
|  | 8.3 | ft + | 38 | ft + | 8.3 | ft = | 54.6 | ft
|  | Final Dimensions (slope >1%) |  | 35.3 | ft x | 54.6 | ft
G. | SAND VOLUME
1. | Upslope Volume + Volume under rockbed + Downslope Volume
a. Upslope Volume:
(depth of clean sand + 1) x (upslope berm) x (mound length) / 2 = ft3
| 2 | ft x | 8.3 | ft x | 54.6 | ft / 2 = | 453.18 | ft3
b. Volume under rockbed:
(average depth of sand under rock) x (rockbed width) x (mound length) = ft3
| 1.15 | ft x | 10 | ft x | 54.6 | ft = | 627.9 | ft3
c. Downslope Volume: (depth of clean sand + 1) x (downslope berm) x (mound length) / 2 = ft3
| 2.3 | ft x | 17 | ft x | 54.6 | ft / 2 = | 1067.43 | ft3
[5 empty] | Total cubic feet: | = | 2148.51 | ft3
2. | Cubic yards
Divide ft3 by 27 ft3/yd3
|  | 2148.51 | / 27 = | 79.5744 | yds3
3. | Weight of sand in tons
Multiply cubic yards by 1.4 to get
|  | 79.5744 | yds3 x 1.4 | 111.4042 | tons
4 | Add 10% for Constructability
|  | 111.4042 | tons x 1.1 = | 122.5446 | tons
H. | ROCK VOLUME
1. | Cubic feet of rock (Area of rock*depth of rock)
|  | 380 | X | 1 | ft = | 380 | ft3
Depth of rock layer
2. | Cubic yards (Divide ft3 by 27 ft3/yd3)
|  | 380 | ft3 / 27 = | 14.0741 | yd3
3. | Weight of rock in tons (cubic yards * 1.4)
|  | 14.0741 | yd3 X 1.4 ton/yd3 = |  | 19.7037 | tons
18 " at peak - top 6" topsoil
12" cover - top 6" topsoil
Restrictive Layer
Original grade

## AtGrade
At Grade |  |  |  | Tax ID #: | 2345
911 Address:
A. | Average Design Flow
[13 empty] | Upslope Width (E2d) | 7.14 | ft
Estimated |  | 450 | gpd
ft
B. | Minimum Septic Tank Capacity | [7 empty] | 25.34
[10 empty] | Upslope Width |  |  | Rock Bed |  | Upslope Width (E2f)
| Septic tank capacity |  | 1500 | gallons | [5 empty] | (E2d) | 7.14 |  | Width(D1) | 13.2 | ft |  | 7.14 | ft
| Effluent filter (yes/no) |  | No | [5 empty] | Total Width (E4) |  |  |  | Length (E5) | 75 | ft
| Number of tanks/compartments |  | 1
C. | SOILS (Site evaluation data)
1 | Depth to restricting layer |  | 4 | ft | [8 empty] | Downslope Width (E3f) | 18.2 | ft
2 | Texture |  | Clay Loam
3 | Soil Sizing Factor (SSF) |  | 2.2 | ft2/gpd
4 | Linear Loading Rate (LLR) |  | 6 | gpd/ft
5 | Land Slope |  | 3 | %
6 | Percolation rate if available |  | 45 | MPI
[12 empty] | Total Length (E6) |  | 89.28 | ft
D. | Rock Width
Rock absorption width equals LLR(C5) times SSF(C4) =
| 6 | gpd/ft x | 2.2 | ft2/gpd = | 13.2 | ft
E. | System Size
1 | The height of the system is |  | 2 | feet
2 | Determine upslope berm width
| a. Upslope multiplier based on percent land slope |  |  |  |  | 3.57
Rock Width (D1)
| b. On slopes > 1%, Upslope width = upslope multiplier(E2a) times system height (E1) | [12 empty] | 13.2 | ft
| 3.57 | ft x | 2 | ft = | 7.14 | ft
c. On slopes < 1%, upslope width equals( 0.5 x absorption width) + 5 ft
| 0.5 | x | 13.2 | + 5 ft = | 11.6 | ft
Rock Width (D1)
| d. Choose 2b or 2c depending on slope | [12 empty] | 13.2 | ft
|  | 7.14 | ft
[11 empty] | Upslope Berm (E2d) |  |  |  | Downslope Berm (E3f)
[11 empty] | 7.14 | ft |  |  | 18.2 | ft
3 | Determine downslope berm width
| a. Downslope multiplier based on percent land slope |  |  |  |  | 4.54
b. Downslope width = downslope multiplier(E3a) times system height (E1)
| 4.54 | ft x | 2 | ft = | 9.08 | ft
c. Rock absorption width (D1) + 5 feet =
|  | 13.2 | + 5ft = | 18.2 | ft
d. On slopes >1%, downslope width equals the larger of 3b and 3c
|  | 18.2 | ft
e. On slopes < 1% downslope width equals 0.5 X absorption width +5 ft
| 0.5 | x | 13.2 | + 5 ft = | 11.6 | ft
f. Choose 2d or 2e depending on slope
|  | 18.2 | ft
4 | System width is the sum of upslope width(E2d) plus downslope width(E3f)
| 7.14 | ft + | 18.2 | ft = | 25.34 | ft
5 | The rock layer length is the flow (A) divided by the LLR(C5)
| 450 | gpd / | 6 | gpd/ft = | 75 | ft
6 | Total length is the sum of upslope width(E2d), rock layer length(E5) and upslope width (E2d)
| 7.14 | ft + | 75 | ft + | 7.14 | ft = | 89.28 | ft
F. | Rock Volume
1 | Rock Area = Length(E5) x Width(D1+ 1ft)
| 75 | ft x ( | 13.2 | ft + 1ft) = | 1065 | ft2
2 | Multiply rock area(F1) by depth of rock(1ft) and divide by 2
because the shape is triangular
| 1065 | ft2 x 1ft /2 = | 532.5 | ft2
3 | Volume in cubic yards = volume in cubic feet divided by 27
| F2/ 27 = cubic yards |  | 532.5 | / 27= | 19.7222 | yd3
4 | Weight of rock in tons = cubic yards times 1.4
| F3 x 1.4 = tons |  | 19.7222 | x 1.4= | 27.6111 | tons
5 | Add in 10% extra for constructability = |  |  | 1.1 x | 27.6111 | = | 30.3722 | tons
Minimum of 2 inches of rock above and around pipe
9 inches
rock minimum
12 inches loamy or sandy cover material
with the top 6 inches being topsoil
4:1 Maximum Side Slopes
1.5 inch minimum diameter
inspection pipe - 3 required

## PresDist
Pressure Distribution | [5 empty] | Tax ID#: | 2345
911 Address:
1. | Select number of perforated laterals: |  |  |  | 4
2. | Select perforation spacing = |  |  | 3 | ft
3. | Since perforations should not be placed closer that 1 foot to
the edge of the rock layer (see diagram), subtract 2 feet from
the rock layer length
|  | 38 | - 2 ft = | 36 | ft
4. | Determine the number of spaces between perforations.
Divide the length (3) by perforation spacing (2) and round down to nearest whole number.
|  | Perforation spacing = |  | 36 | ft / | 3 | ft = | 12 | ft
5. | Select perforation size |  |  | 0.25 | inch
6. | Number of perforations is equal to one plus the number of perforation spaces (4).
* Check figure E-4 to assure the number of perforations per lateral guarantees
< 10% discharge variation.
| 12 | spaces + 1 = |  | 13 | perforations/lateral
7. | A. Total number of perforations = perforations per lateral (5) times number of laterals (1).
| 13 | perfs/ lat x | 4 | laterals = | 52 | perforations
B. Calculate the square footage per perforation.
Recommended value is 6-10 sqft/perf. Does not apply to at-grades.
1. Rock bed area = rock width (ft) x rock length (ft)
| 10 | ft x | 38 | ft = | 380 | ft2
2. Square foot per perforation=Rock Bed Area/number of perfs(6)
| 380 | ft2 / | 52 | perfs = | 7.3077 | ft2/ perf |  | Should be between X and X
8. | Determine required flow rate by multiplying the total number
of perforations(6A) by flow per perforations (see figure E-6)
|  | 52 | perfs x | 0.74 | gpm / perfs = |  | 38.48 | gpm
9. | Determine Minimum Pipe Size
A. | Manifold on End. If laterals are connected to header pipe
as shown in Figure E-1, to select minimum required lateral
diameter; enter figure E-4 or E-5 with perforation spacing and
number of perforations per lateral. Select minimum diameter
| for perforated laterals = |  |  | 2 | inches
B. | Center Manifold. If perforated lateral system is attached to
| manifold pipe near the center, like Figure E-2, perforated lateral length (3) | [6 empty] | Number of Perfs/lateral |  | 13
| and number of perforations per lateral (5) will be approximately | [6 empty] | Perf Spacing |  | 3 | ft
| one half of that in step A. Using these values, select | [6 empty] | Perf Size |  | 0.25 | inch
| minimum diameter for perforated lateral = |  |  |  |  | inches
Note:
Fill in either 9A or 9B.
Do NOT fill in both.

## Pump
Pump |  |  |  |  | Tax ID#: | 2345
911 Address:
1. | Determine pump capacity:
A. Gravity Distribution
1. Minimum required discharge is 10 gpm
2. Maximum suggested discharge is 45 gpm
For other establishments at least 10% greater than the water
supply rate, but no faster than the rate at which effluent will flow
out of the distribution device.
B. Pressure Distribution - see pressure design worksheet
| Pump Capacity: |  |  | 38.48 | gpm
2. | Determine Total Dynamic Head (TDH)
A. | Elevation difference between pump and point of discharge.
| 7 | feet
B. | Special head requirement? (See Figure - Special Head Requirements)
| 5 | feet
C. | Friction loss in supply pipe
| 1. Select pipe diameter |  | 2 | in
2. Enter Figure E-9 with gpm (1A or B) and pipe diameter (C1)
Read friction loss in feet per 100 feet from Figure E-9
| Friction loss= | 1.55 | ft/ 100 ft of pipe (figure E-9)
3. Determine total pipe length from pump discharge to soil system discharge point.
Estimate by adding 25 percent to pipe length for friction loss in fittings.
Pipe length times 1.25 = equivalent pipe length
| 35 | ft x 1.25 = | 43.75 | feet
Est. Pipe length
4. Calculate total friction loss
by multiplying friction loss (C2) by the equivalent pipe length (C3) and divide by 100.
| Friction Loss = | 1.55 | ft/100ft X | 43.75 | ft / 100 = | 0.67812 | feet
5. | Total head requirement
is the sum of elevation difference (A), special head requirments (B), and total friction loss (C4)
| 7 | ft + | 5 | ft + | 0.67812 | ft
| Total Head: |  | 12.6781 | feet
6. | Pump Selection
| 1. A pump must be selected to deliver at least |  |  |  | 38.48 | gpm (1A or B)
| with at least | 12.6781 | feet of total head (2D).

## Non-Level
Non-Level | [6 empty] | Tax ID #: | 2345
911 Address:
1. | Enter each system lateral elevation and length in order of highest to lowest elevation
|  | Lateral 1 | Elevation = |  |  | ft | Length of pipe |  |  | ft
|  | Lateral 2 | Elevation = |  |  | ft | Length of pipe |  |  | ft
|  | Lateral 3 | Elevation = |  |  | ft | Length of pipe |  |  | ft
|  | Lateral 4 | Elevation = |  |  | ft | Length of pipe |  |  | ft
|  | Lateral 5 | Elevation = |  |  | ft | Length of pipe |  |  | ft
|  | Lateral 6 | Elevation = |  |  | ft | Length of pipe |  |  | ft
2. | Calculate change in elevation over the laterals.
| Highest elevation - lowest elevation: |  |  |  |  | 0 | - | 0 | = | 0 | feet
3. | Calculate the Total Head = head at orifices (either 1 or 2 ft) + change in elevation(2)
Enter 1 ft if design if for a single family home or 2 ft for anything else (min design pressure head at perforation)
| 2 | ft + | 0 | ft = |  | 2 | feet
This worksheet can not be used if greater than 5 feet. Design must be modified or valving must be used to equalize flow.
4. | Calculate pressure head for each lateral
1. Highest Trench Elevation (E1) the Head = 1 or 2 feet (baseline head)
2. For all other laterals the pressure head is calculated as baseline head plus the change in elevation from Lateral 1.
| Lateral 1 | Elevation | 0 | [9 empty] | 2 | ft
| Lateral 2 | Elevation | 0 | 0 | + [E1 - E2] = |  | 0 | + [ | 0 | - | 0 | ] = | 0 | ft
| Lateral 3 | Elevation | 0 | 0 | + [E1 - E3] = |  | 0 | + [ | 0 | - | 0 | ] = | 0 | ft
| Lateral 4 | Elevation | 0 | 0 | + [E1 - E4] = |  | 0 | + [ | 0 | - | 0 | ] = | 0 | ft
| Lateral 5 | Elevation | 0 | 0 | + [E1 - E5] = |  | 0 | + [ | 0 | - | 0 | ] = | 0 | ft
| Lateral 6 | Elevation | 0 | 0 | + [E1 - E5] = |  | 0 | + [ | 0 | - | 0 | ] = | 0 | ft
5. | Determine flow rate per hole (See figure E-6).
Select a perforation diameter and the corresponding gallons per minute interpolating as needed.
| Lateral 1 | Pres | 2 |  | Perf | Diameter |  |  | = |  | gpm
| Lateral 2 | Pres | 0 |  | Perf | Diameter |  |  | = |  | gpm
| Lateral 3 | Pres | 0 |  | Perf | Diameter |  |  | = |  | gpm
| Lateral 4 | Pres | 0 |  | Perf | Diameter |  |  | = |  | gpm
| Lateral 5 | Pres | 0 |  | Perf | Diameter |  |  | = |  | gpm
| Lateral 6 | Pres | 0 |  | Perf | Diameter |  |  | = |  | gpm
6. | Calculate flow in gallons per minute for Lateral 1 - Select a spacing and enter in box.
Number of perforations
[(length of pipe - 2)/spacing] +1
| [( | 0 | ft - 2ft) / |  | 3 | ft]+1 = | 1 | perforations (Check figure E-4 to make sure it is ok)
Spacing
Flow
number of perforations x flow rate
|  | 1 | perf x |  | 0 | gpm = |  | 0 | gpm for Lateral 1
7. | Calculate the gallons per minute per foot for Lateral 1
This value will then be used to make sure the gallon per minute per foot is equivalent in each lateral.
| Gallons / length = |  | 0 |  | gpm / | 0 | ft = | 0 | gpm/ ft
8. | Balance flows for other lengths, spacing, or size.
If you end up with a large spacing ( 5' is max) lower the initial spacing in #6 or the perf size in #5.
| Lateral 2 | GPM = length of pipe x gallons per minute per foot (7)
|  |  | 0 |  | ft x | 0 | gpm/ft = |  | 0 | gpm
# of Perfs = GPM / flow rate(5.2)
|  |  | 0 |  | gpm / | 0 | gpm = | 0 | # of Perfs (Check figure E-4)
Spacing = (Length - 2 feet) / (Number of perfs -1)
| ( | 0 | ft - 2ft) / ( |  | 0 | perfs - 1) = |  | 0 | feet
| Lateral 3 | GPM = length of pipe x gallons per minute per foot (7)
|  |  | 0 |  | ft x | 0 | gpm/ft = |  | 0
# of Perfs = GPM / flow rate(5.3)
|  |  | 0 |  | gpm / | 0 | gpm = | 0 | # of Perfs (Check figure E-4)
Spacing = (Length - 2 feet) / (Number of perfs -1)
| ( | 0 | ft - 2ft) / ( |  | 0 | perfs - 1) = |  | 0 | feet
| Lateral 4 | GPM = length of pipe x gallons per minute per foot (7)
|  |  | 0 |  | ft x | 0 | gpm/ft = |  | 0
# of Perfs = GPM / flow rate(5.4)
|  |  | 0 |  | gpm / | 0 | gpm = | 0 | # of Perfs (Check figure E-4)
Spacing = (Length - 2 feet) / (Number of perfs -1)
| ( | 0 | ft - 2ft) / ( |  | 0 | perfs - 1) = |  | 0 | feet
| Lateral 5 | GPM = length of pipe x gallons per minute per foot (7)
|  |  | 0 |  | ft x | 0 | gpm/ft = |  | 0
# of Perfs = GPM / flow rate(5.5)
|  |  | 0 |  | gpm / | 0 | gpm = | 0 | # of Perfs
Spacing = (Length - 2 feet) / (Number of perfs -1)
| ( | 0 | ft - 2ft) / ( |  | 0 | perfs - 1) = |  | 0 | feet
| Lateral 6 | GPM = length of pipe x gallons per minute per foot (7)
|  |  | 0 |  | ft x | 0 | gpm/ft = |  | 0
# of Perfs = GPM / flow rate(5.5)
|  |  | 0 |  | gpm / | 0 | gpm = | 0 | # of Perfs
Spacing = (Length - 2 feet) / (Number of perfs -1)
| ( | 0 | ft - 2ft) / ( |  | 0 | perfs - 1) = |  | 0 | feet
9. | Calculate total gpm for system - the total GPM need from the pump
| Lateral 1 | Flow = | 0 |  | gpm
| Lateral 2 | Flow = | 0 |  | gpm
| Lateral 3 | Flow = | 0 |  | gpm
| Lateral 4 | Flow = | 0 |  | gpm
| Lateral 5 | Flow = | 0 |  | gpm
| Lateral 6 | Flow = | 0 |  | gpm
|  | Total = | 0 |  | gpm
10. | Summary
Enter the minimum pipe size that allows for even distribution and the volume of liquid in the pope (E-20).
|  | Pipe Size | Pipe Vol. |  | Pipe Length |  | Total Volume |  |  | Perf Size |  | Spacing | Spacing
|  | (in) | (gal/ft) |  | (ft) |  | to Fill (gal) |  |  | (in) |  | (ft) | (in)
| Lateral 1 |  |  |  | 0 |  | 0 |  |  | 0 |  | 3 | 36
| Lateral 2 |  |  |  | 0 |  | 0 |  |  | 0 |  | 0 | 0
| Lateral 3 |  |  |  | 0 |  | 0 |  |  | 0 |  | 0 | 0
| Lateral 4 |  |  |  | 0 |  | 0 |  |  | 0 |  | 0 | 0
| Lateral 5 |  |  |  | 0 |  | 0 |  |  | 0 |  | 0 | 0
| Lateral 6 |  |  |  | 0 |  | 0 |  |  | 0 |  | 0 | 0
[6 empty] | Total = | 0 |  | gallons
This is the total volume to fill the laterals
Amount per Dose should be 4-5 times this.

## Dosing
Dosing Chamber Sizing |  |  |  |  | Tax ID #: | 2345
911 Address:
1. | Determine area
A. Rectangle area = L x W
|  | 4 | ft x | 5 | ft = | 20 | ft2
B. Circle area = 3.14 x radius2
|  | 3.14 x |  | 2 ft = | 0 | ft2
| C. Get area from manufacture |  |  |  | ft2
2. | Calculate gallons per inch
There are 7.5 gallons per cubic foot of volume, therefore multiply the area (1A, B or C)
times the conversion factor and divide by 12 inches per foot to calculate gallon per inch.
| Surface area x 7.5 / 12 = |  | 20 | ft2 x 7.5 / 12in/ft = |  | 12.5 | gallon per inch
3. | Calculate total tank volume | [7 empty] | Legal Tank:
500 gallons or
| A. Depth from bottom of inlet pipe to tank bottom = |  |  |  | 39 | in |  |  | 100% the daily flow
or Alternating Pumps
B. Total tank volume
depth from bottom of inlet pipe to tank bottom(3A) x gal/in(2)
| = | 39 | in x | 12.5 | gal/in = | 487.5 | gallons
4. | Calculate gallons to cover pump
(with 2-3 inches of water covering pump) (Pump and block height + 2 inches) x gallon per inch
| ( | 8 | in + 2 in) x | 12.5 | gal/in = | 125 | gallons
Pump and Block Height
5. | Calculate total pumpout volume
A. Select pump size for 4-5 doses per day.
Gallon per dose = gpd (see Figure A-1)/ doses per day =
| 450 | gpd / | 3 | doses/day = | 150 | gallons
B. Calculate drainback
| 1. Determine total pipe length |  |  | 35 | ft
| 2. Determine liquid volume of pipe, |  |  | 0.17 | gal/ft | Pipe Diam. | 2 | inches
| 3. Drainback quantity = |  | 35 | ft (5B1) x | 0.17 | gal/ft(5B2) = | 5.95 | gal
C. Total pump out volume
dose volume(5A) + drainback (5B3)
|  | 150 | gallons + | 5.95 | gallons = | 155.95 | gal
6. | Calculate float separation distance
(using total pumpout volume) Total pumpout volume(5C) / gal/inch(2)
| 155.95 | gal / | 12.5 | gal/in = | 12.476 | inch
7. | Calculate volume for alarm
Alarm depth (inch) x gallon/inch(2)
|  | = | 3 | in x | 12.5 | gal/in = | 37.5 | gal
(typically 2 - 3 inches)
8. | Calculate total gallons
gallons over pump(4) + gallons pumpout(5C) + gallons alarm(7)
| 125 | gal + | 155.95 | gal + | 37.5 | gal = | 318.45 | gal
9. | Total tank depth
total gallons(8) / gallon/in(2)
| 318.45 | gallons / | 12.5 | gal/in = | 25.476 | in
Recommended
Calculate reserve capacity (75% of the daily flow)
Daily flow x 0 .75 = |  |  | 450 | x 0.75 = | 337.5 | gallons
Width
Length
Radius

## Summary Sheet
SSTS Design Summary |  |  |  | Tax ID#: | 2345
911 Address:
Mound Design Summary
Area of Rock | 380 | ft2 |  | Rock Layer Width |  | 10 | ft
Rock Layer Length | 38 | ft
<1%
Depth of Clean Sand | 1 | ft |  | Additional Width for Absorption |  | -7 | ft
Mound Height | 3 | ft |  | Final Berm Width |  | 5 | ft
Berm Width | 12 | ft |  | Total Mound Width |  | 34 | ft
Total Landscape Width | 34 | ft |  | Total Mound Length |  | 62 | ft
Setbacks from Rock Layer | 8.5 | ft |  |  | Absorbtion Width | 27 | ft
>1%
Upslope Depth of Clean Sand | N/A | ft |  | Downslope Mound Height |  | N/A | ft
Mound Height Upslope Edge | N/A | ft |  | Downslope Berm Multiplier |  | N/A | ft
Upslope Width | N/A | ft |  | Downslope Width |  | N/A | ft
Downslope Drop in Elevation | N/A | ft |  | Total Mound Width |  | N/A | ft
Absorbtion Width | N/A | ft |  | Total Mound Length |  | N/A | ft
Trench or Bed
Trench 6" Sidewall | N/A | ft2 | Pressure Beds 6 or 12" of Rock |  |  | N/A | ft2
Trench 12" Sidewall | N/A | ft2
Trench 18" Sidewall | N/A | ft2
Trench 18" Sidewall
Trench 24" Sidewall | N/A | ft2
Gravity Bed 6 or 12" of Rock | N/A | ft2
At Grade
Rock Width | N/A | ft |  | Height of System |  | N/A | ft
Rock Length | N/A | ft |  | Upslope Berm Width |  | N/A | ft
Rock Area | N/A | ft2 |  | Downslope Berm Width |  | N/A | ft
Cubic Yards Rock | N/A | yd3 |  | Total Length |  | N/A | ft
Weight of Rock | N/A | tons
Pressure Distribution Summary
Number Perf. Laterals | 4 |  |  | Square Feet Per Perforation |  | 7.3077 | ft2
Perforation Spacing | 12 | ft |  | Required Flow Rate |  | 38.48 | gpm
Perforation Size | 0.25 | in |  | Minimum Pipe Size |  | 2 | in
Number of Perforations | 52
Rock Bed Area | 380 | ft2 | Rock Bed Area for Mound Systems. If Trench, Bed or At-Grade Design Utilize Above Areas.
Dosing Chamber Summary
Area | 20 | ft2 |  | Total Pump Out Volume |  | 150 | gal
Gallons per Inch | 12.5 | GPI |  | Float Seperation Distance |  | 12.476 | in
Total Tank Volume | 487.5 | gal |  | Volume for Alarm |  | 37.5 | gal
Gallons to Cover Pump | 125 | gal |  | Total Tank Depth |  | 25.476 | in
I hereby certify that I have completed this work in accordance with all applicale ordinances, rules and laws.
|  | (signature) | 45678 |  | (licence #) |  | (date)
Local Unit of Government Approval
|  | (signature) |  |  | (registration #) |  | (date)